# Valve actuator: SAUTER vialoq AVM 1000 Retrofit

Make:   AVM322F122R

## Area of application

In ventilation and air conditioning systems for actuating 2-way and 3-way valves of the V6*, VQD, VQE, VUG, VUP, VUS, B6*, BQD, BQE, BUG, BUS series and non-SAUTER valves like Siemens, JCI, Honeywell, LDM, ITT-Träger, Belimo, Frese.

For controllers with a switching output (2-point or 3-point control).

## Performance features

- Valve actuator with patented actuator/valve coupling (quick-release).

- Low energy consumption.

- Crank handle for external manual adjustment with motor cut-off.

- Electrical connection using plug-in screw terminals up to 1.5 mm².

- With low-noise gear unit and electric, power-dependent motor cut-off.

## Technical data

General information

| Power supply: | 24 V~/= |
| --- | --- |
| Actuating power: | 1000 N |
| Stroke: | 20 mm |
| Selectable positioning time: | 6 or 12 s/mm |
| Inputs: | 2-point or 3-point |
| Operating noise: | < 30 dB(A) |
| Connection module: | Pluggable screw terminal for conductor cross-section of max. 1.5 mm2 |
| Dimensions, W x H x D: | 160 x 187 x 88 mm |

Power consumption

| During operation: | < 2.0 W < 3.0 VA |
| --- | --- |
| At standstill: | < 0.3 W |

Admissible ambient conditions

| Operating temperature: | -10…55 °C |
| --- | --- |
| Storage and transport temperature: | -40…80 °C |
| Humidity: | 5…85% rh |
| Ingress protection: | IP 54 |

Accessories

| 0510600001 | Cable module, 1.2 m, 3-wire, PVC |
| --- | --- |
| 0510600002 | Cable module, 1.2 m, 3-wire, halogen-free |
| 0510600003 | Cable module, 1.2 m, 6-wire, PVC |
| 0510600004 | Cable module, 1.2 m, 6-wire, halogen-free |
| 0510600005 | Cable module, 5 m, 3-wire, PVC |
| 0510600006 | Cable module, 5 m, 3-wire, halogen-free |
| 0510600007 | Cable module, 5 m, 6-wire, PVC |
| 0510600008 | Cable module, 5 m, 6-wire, halogen-free |
| 0510390020 | Adaptations for SAUTER valves VUD/BUD DN 65…80 VUE/BUE DN 65…80 VUG/BUG DN 15…50, VUP DN 40 |
| 0510390021 | Adaptations for SAUTER valves V6/B6 Retrofit V6R/B6R DN 15…50, V6F/B6F DN 15…50, V6G/B6G DN 15…50, V6S/B6S DN 15…50 |
| 0510390022 | Adaptations for non-SAUTER valves by Siemens VVF21 DN 25…80, VXF21 DN 25…80, VVF31 DN 15…80, VXF31 DN 15…80, VVF40 DN 15…80, VXF40 DN 15…80, VVF41 DN 50 |
| 0510390023 | Adaptations for non-SAUTER valves by JCI VBD-4xx4 DN 15...40, VBD-4xx8 DN 15...40, VBF-2xx4, VBF2xx8, VBB-2xxx, VG82xx, VG84xx, VG88xx VG89xx |
| 0510390024 | Adaptations for non-SAUTER valves by Honeywell V5025A DN 15...80, V5049A or B DN 15...65, V5049B DN 15…65, V5050A DN 15...80, V5095A DN 15...80 |
| 0510390025 | Adaptations for non-SAUTER valves by LDM RV113 R/M DN 15…80 |
| 0510390026 | Adaptations for non-SAUTER valves by ITT-Dräger PSVF DN 15...32, PSVD DN 15...32, SVF DN 15...32, SVD DN 15...32 |
| 0510390027 | Adaptations for non-SAUTER valves by Belimo H6..R DN 15...65, H7...R DN 15...65, H4...B DN 15...50, H5..B DN 15...50, H6…N DN 15...65, H7...N DN 15…65 |
| 0510390028 | Adaptations for non-SAUTER valves by Frese Optima Compact DN 50…80 |

Manufacturer: Fr. Sauter AG, Basel